# Tab 1

# Stormwater Trench and Slot Drains - Landscape Drains Section 33 42 36 This guide specification was developed for Landscape Drains, a Division of Global Drain Technologies Slot, Trench drains, and Catch Basins. Edit bracketed selections and delete items not required for the Project.

### Global Drain Technologies 855 497 7508 info@globaldraintech.com globaldraintech.com

# PART 1 - GENERAL

## 1.1 SUMMARY

- Section Includes:

  - Slot Drains.

  - Trench Drains.

  - Catch Basins.

- Related Requirements:

  - Section ​​​031000-Concrete Forming and Accessories.

  - Section ​​​033000-Cast-in-Place Concrete​​​.

  - Section ​​​334211-Stormwater Gravity Piping.

## 1.2 REFERENCE STANDARDS

- ADA Standards - 2010 ADA Standards for Accessible Design.

- DIN EN 1433 - Drainage Channels for Vehicular and Pedestrian Areas - Classification, Design and Testing Requirements, Marking and Evaluation of Conformity.

## 1.3 ADMINISTRATIVE REQUIREMENTS

- Preinstallation Meeting: Convene meeting [1 week] [2 weeks] before starting Work of this Section.

- Required Attendees: [Contractor] [Architect] [installer] [manufacturer's representative], and other parties directly affecting Work of this Section.

- Review the following:

- Materials.

- Installation sequence and tolerances.

- Adjustment requirements.

- Cleaning and maintenance procedures.

- Protection of installed Work.

- Coordination with concrete, flooring, elevator, and plumbing work.

## 1.4 SUBMITTALS

- Submit under Division 01 requirements.

- Action Submittals:

- Product Data: Manufacturer's literature and data sheets for each product, including fabrication materials, components, dimensions, ratings, finishes, rough-in requirements, accessories, and installation instructions.

- Shop Drawings - [Slot Drains] [Trench Drains]: Plans or diagrams showing layout of individual drains and drain networks; length and width of each drain; starting and ending inverts; sanitary waste piping connection points; catch basins; and accessories.

- Samples: Manufacturer's drain sample.

- Informational Submittals:

- Manufacturer's certification that products comply with specified requirements and are suitable for intended application.

- Manufacturer's project references for successfully completed, slot, or trench drainage channel system projects, including project name and location, Architect, type of system, and quantity furnished.

- Installer's project references for successfully completed slot, or trench drainage channel system projects, including project name and location, Architect, type of system, and quantity installed.

- Manufacturer's written instructions for handling, protection, examination, preparation, and installation of elevator threshold drains, elevator lobby drains, slot drains, trench drains, and catch basins.

- Warranty Documentation: Manufacturer's standard warranty.

## 1.5 QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in products specified in this Section with minimum [10] [__] years of [documented] experience manufacturing similar drainage channel systems.

- Project References - Slot and Trench Drains: List of [ten] [__] completed slot or trench drain projects, including project name and location, Architect, type of system, and quantity furnished.

- Installer Qualifications: Installer regularly engaged in installation of similar drainage channel systems for minimum [5 years] [__] and approved by manufacturer.

- Employ persons trained in installation of drainage channel systems.

- Provide a list of ten completed slot, or trench drain projects, including project name and location, Architect, type of system, and quantity installed.

## 1.6 DELIVERY, STORAGE, AND HANDLING

- Deliver materials in manufacturer's original, unopened containers and packaging with labels clearly identifying product name and manufacturer.

- Store and handle materials in accordance with manufacturer's written instructions.

- Keep materials in original, unopened containers and packaging until installation.

- Store materials in clean areas protected from harmful weather and direct sunlight.

- Protect materials during storage, handling, and installation to prevent damage.

## 1.7 FIELD CONDITIONS

- Ambient Conditions:

- Do not use frozen materials or materials mixed or coated with ice or frost.

- Do not install products on frozen subgrade.

- Do not install products on wet, saturated, or muddy subgrade.

- Wet Weather: Do not install products on wet, saturated, or muddy subgrade.

# PART 2 - PRODUCTS

## 2.1 MANUFACTURERS

- Basis-of-Design Manufacturer: Landscape Drains, a Division of Global Drain Technologies , 7421 S 42nd Street, Suite 6, Grand Forks, ND 58291; 100 McPhillips Street, Winnipeg, MB R3E 2J7; phone 855.497.7508; website https://globaldraintech.com/; email orders@globaldraintech.com.

- Basis of Design: Landscape Drains drainage channel systems.

- Substitutions: Not permitted.

- Source Limitations: Furnish products [produced by a single manufacturer] [obtained from single supplier].

## 2.2 GENERAL PRODUCT REQUIREMENTS

- Materials: Conform to requirements specified in this Section and applicable reference standards.

- Stainless Steel: [Type 304] [Type 316] stainless steel, unless otherwise indicated.

- Finish: 2B mill finish

- Accessible Walking Surfaces: Provide grates and slot openings complying with ADA Standards and heel-proof requirements where exposed to pedestrian traffic.

- Tamper Resistance: Provide tamper-resistant exposed grates and grate locks where indicated.

- Fasteners: Provide stainless steel fasteners compatible with the stainless steel used within the drainage system.

## 2.3 SLOT DRAINS

- Basis-of-Design Products:

- Landscape Drains 7,000 Series.

- Landscape Drains 7,000 Radius Series.

- Landscape Drains 6,000 Series.

- Landscape Drains 4,000 Series.

- Landscape Drains 4,000 Radius Series.

- Landscape Drains 3,000 Series.

- Description: Slot drain system assembled from factory-formed channels; includes leveling brackets, tie-down anchors, end caps, and outlet fittings.

| Drain Series | Slope | Standard Slot Widths (in) | Flow Rate (GPM) Minimum Discharge | Flow Rate (GPM) @ 96.7' Length Discharge | Material | Load Class (ASME/DIN) |
| --- | --- | --- | --- | --- | --- | --- |
| 7000 | 0.5% | 0.50 | 17.99 | 128.35 | [304][316] SS] | Medium Duty/Class C |
| 7000 | 1% | 0.50 | 17.99 | 250.40 | [304][316] SS] | Medium Duty/Class C |
| 7000 Radius | 0.5% | 0.50 | 17.99 | - | [304][316] SS] | Medium Duty/Class C |
| 6000 | 0.5% | 0.50/1.00 | 20.11 | 134.69 | [304][316] SS] | Light Duty/Class B |
| 6000 | 1% | 0.50/1.00 | 20.11 | 258.24 | [304][316] SS] | Light Duty/Class B |
| 4000 | 0.5% | 0.50 | 14.62 | 124.96 | [304][316] SS] | Medium Duty/Class C |
| 4000 | 1% | 0.50 | 14.62 | 249.16 | [304][316] SS] | Medium Duty/Class C |
| 4000 Radius | 0.5% | 0.50 | 14.62 | - | [304][316] SS] | Medium Duty/Class C |
| 3000 | 0% | 0.50 | 21.10 | 21.10 | [304][316] SS] | Medium Duty/Class C |

*select above specific to the project requirements

- Materials and Finish:

- Drain Material: Type [304] [316] stainless steel, minimum 16 gauge, 0.060 inch (1.5 mm). Provide drain, accessories, and appurtenances in same stainless steel type.

- Drain Material Radius Series: Type [304] [316] stainless steel, minimum 16 gauge, 0.0625 inch (1.59 mm). Provide drain, accessories, and appurtenances in same stainless steel type.

- Finish: 2B mill finish.

- Performance:

- DIN EN 1433: Load Class [B] [C] [as indicated].

- Channel Joints: [Welded] [Flanged, with manufacturer-provided fasteners and sealants].

- ADA Compliance: [Standard slot opening] [Heel-proof slot opening complying with ADA Standards for Accessible Design]

- Channel Parameters:

- Slope: [0.5 percent] [1.0 percent] [Stepped slope, as indicated on drawings].

- Slot Width and Flow Rate: Provide drains with the following slot width and corresponding minimum flow rate per linear foot (30 cm) of drain:

- 1/2-inch (13 mm) slot width; 11 gpm (43 L/min) flow rate.

- 1-inch (25 mm) slot width; 18 gpm (68 L/min) flow rate.

- 1-1/4-inch (32 mm) slot width; 27 gpm (102 L/min) flow rate.

- 3/16 x 2 (5 mm x 2) slot width; 8 gpm (30 L/min) flow rate.

- Inside Starting Depth:

- 7000 Series: 4-1/2 inches (114 mm).

- 7000 Series Radius: 4-1/2 inches (114 mm).

- 6000 Series: 2-11/16 inches (68 mm).

- 4000 Series: 4-1/2 inches (114 cm).

- 4000 Series Radius: 4-1/2 inches (114 cm).

- 3000 Series Radius: 7-1/4 inches (184 cm).

- Accessories:

- Catch basins: As specified in Article 2.5.

- Closed end caps.

- Flush-Flo End Cap: Manufacturer's end cap with 1-inch NPT threaded fitting.

- Custom fittings: end cap with outlet, bottom outlet fitting, side outlet fitting.

- Cleaning Brush: Manufacturer's matching cleaning brush.

- Cleaning Paddle: Manufacturer's matching cleaning paddle.

- Slot Dog: Manufacturer's high-pressure drain cleaning tool.

- 0.50 Inch Pressure Washer Nozzle: Manufacturer's high-pressure drain cleaning tool.

## 2.4 TRENCH DRAINS

- Basis-of-Design Products:

- Landscape Drains Trench Drain - Flat.

- Description: Trench drain system assembled from factory-formed channels with integral, formed grate-support edge; includes leveling brackets, tie-down anchors, end caps, outlet fittings, and grating.

- Materials and Components:

- Drain Material: Type [304] [316] stainless steel, minimum 16 gauge, 0.060 inch (1.5 mm). Provide drain, accessories, and appurtenances in same stainless steel type.

- Grate: Stainless steel, manufacturer provided.

- Grate Style: [Standard perforated] [Modern slotted] [Designer wave]

- Grate Height: [0.5 inches (13 mm)] [0.75 inches (19 mm)] [1.00 inches (25 mm)].

- Finish: 2B mill finish.

- Performance:

- DIN EN 1433: Load Class [A] [B] [as indicated].

- ASME A112.6.3/CSA B79.3 or ASME A112.6.8/CSA B79.8: Light Duty

- Channel Joints: [Welded] [Flanged, with manufacturer-provided fasteners and sealants].

- Channel Parameters:

- Slope: [0.5 percent] [1.0 percent] [Stepped slope, as indicated on drawings].

- Width: 5 inches (127 mm).

- Minimum Flow Rate:

- [Standard perforated: 8 gpm (30.28 L/min) per linear foot (30 cm) of drain.]

- [Modern slotted: 6 gpm (27.71 L/min) per linear foot (30 cm) of drain.]

- [Designer wave: 6 gpm (27.71 L/min) per linear foot (30 cm) of drain.]

- Inside Starting Depth:

- Flat Bottom Trench Drains: 4 inches (152 mm).

- Installations with Fluid-Applied Flooring: Provide manufacturer's KeyForm system where required to facilitate adhesion of fluid-applied flooring to stainless steel drains.

- Accessories:

- Catch basins: As specified in Article 2.5.

- Strainer basket.

- Closed end caps.

- Flush-Flo End Cap: Manufacturer's end cap with 1-inch NPT threaded fitting.

- End cap with outlet.

- Bottom outlet fitting.

- Side outlet fitting.

- Grate Clips: Manufacturer's clip-in anchoring system to prevent rocking or slipping.

- Grate Locks: Manufacturer's vandal-resistant locking devices.

- Clean-in-Place Stopper: Manufacturer's custom-fit drain plug.

## 2.5 CATCH BASINS

- Stainless Steel Catch Basins, Square:

- Description: Square-bodied catch basin with lid, lid frame, and strainer baskets.

- Basin Material: Stainless steel, minimum 14 gauge, 0.075 inch (1.9 mm). Provide catch basins, accessories, and appurtenances in same stainless steel type and finish as drain system served.

- Load Class: Match or exceed load class of drain system.

- Basin Dimensions:

- Top Width: [6 inches (152 mm)] [7-1/8 inches (181 mm)] [12 inches (305mm)] [____ inches (_____ mm)].

- Top Length: [6 inches (152 mm)] [7-1/8 inches (181 mm)] [12 inches (305mm)] [____ inches (_____ mm)].

- Depth: [12 inches (305 mm)] [20 inches (508 mm)] [____ inches (_____ mm)].

- Lid: [Stainless steel with lift holes] [Stainless steel pan lid].

- Basket Strainer: Perforated stainless steel.

- Outlet:

- Material: [Schedule 40] [Schedule 10] stainless steel.

- Location: [Bottom] [Side, as shown on drawings] [Corner, as shown on drawings] [As indicated on drawings].

## 2.9 ACCESSORIES

- Slot Dog Pressure-Washing Tool

- Basis of Design: Landscape Drains, a division of Global Drain Technologies; Slot Dog Cleaning Tool

- Description: High-pressure, water-based slot drain cleaning tool, with built-in guides, spray nozzle, and cleaning brushes.

- Material: Type 304 stainless steel.

- Pressure Rating: 2,500 psi (17.2 MPa) at 72 degrees F (22 degrees C) and 1,900 psi (13.1 MPa) at 320 degrees F (160  degrees C).

- 0.50 Inch Pressure Washer Nozzle

- Basis of Design: Landscape Drains, a division of Global Drain Technologies; Pressure Nozzle.

- Description: Pressure nozzle that attaches to a pressure washer, allowing for the cleaning of the interior of a slot drain channel.

- Material: Type 304 stainless steel.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

- Verify excavation, trenching, and bedding meet manufacturer's requirements to receive drains.

- Verify rough-ins for field connections match sizes and locations indicated on Drawings.

- Verify field piping connections are at inverts indicated on Drawings.

- Discard packing materials and verify product interiors are free from debris, damage, and corrosion.

- Verify end connections and flanges are clean and without signs of damage or degradation.

- Notify Architect / Engineer of conditions that would adversely affect installation or subsequent use.

- Do not begin installation until unacceptable conditions are corrected.

## 3.2 INSTALLATION

- Install products in accordance with manufacturer's written installation instructions and at locations indicated on Drawings.

- Coordinate installation with cast-in-place concrete, flooring, and plumbing Work.

- Install drains so tops are level and at design elevation.

- Install drains parallel and perpendicular to building lines, unless indicated otherwise on Drawings.

- Installer to ensure all metallic components of the drainage system located within 5 feet (1.5 meters) of the inside walls of the pool—or within the perimeter specified by the local Authority Having Jurisdiction (AHJ)—are strictly bonded to the pool’s equipotential bonding grid.

- Before concrete placement, mask top surfaces of drains [and catch basins].

- Install grates in trench drains so grates do not rock, slip, or shift.

## 3.3 ADJUSTING

- Remove and replace damaged components that cannot be successfully repaired, as determined by Architect / Engineer.

## 3.4 CLEANING

- Remove masking from drains [and catch basins] and clean remaining residue. Use cleaning agents that do not stain, scratch, or mar drains and catch basins.

- Clean debris from drains.

- Clean grates before Substantial Completion.

- Provide maintenance procedures for removal of solids from grates and channels using [manufacturer's brush and paddle accessories] [Slot Dog pressure-washing tool by Global Drain Technologies].

## 3.5 PROTECTION

- Protect installed drains from accumulating dirt and debris through remainder of construction.

- Protect installed products from damage due to subsequent construction operations. Work shall be without damage or deterioration at time of Substantial Completion, except for normal weathering.

END OF SECTION